## Slide 1
Dr. Mahmoud Hassan, PhD, PEng, MCSCE
Dr. Abdulaziz Al-Meshari, PhD
Mr. Hussain H. Al-Wadie
Integrity of Fibre Reinforced Plastic Piping Systems in SABIC plants

## Slide 2: Outline
  Introduction
  Advantages & disadvantages
  Inspection strategy
  Failure modes
  Visual defects

## Slide 3: Introduction
(FRP) is Fiber Reinforced Plastic.
(GRP) is Glass-Reinforced Plastic.
This immaterial has been introduced to the market since 1935.
It can be used for various services including:
    Sea water
    Fire water
    Cooling Water
    and Chemicals.
FRP pipes are fabricated from three distinct layers:
    Liner
    filament layer
    resin coating

## Slide 4: Advantages & Disadvantages
Advantages:
    Corrosion resistance
    Low maintenance cost.
    Good aging resistance.
    Good heat resistance.
    Lightweight, so convenient transportation and construct.
    Lower thermal conductivity.
Disadvantages:
  Low elastic modulus.
  Aging Ex(UV attack, mechanical stress,etc)
  Low fatigue resistance.
  Sensitivity to abrasion during handling.
  Unavailability of inspection techniques.
  Requires very stringent QA/QC during manufacturing and installation.

## Slide 5: Inspection strategy
Inspection of installed FRP systems is mainly done visually.
When damage is observed, ISO-14692-4 and ASTM D2563 provide guidelines on the acceptability of defects.
Inspection of underground FRP piping can be used by:
  Man entry (Dia > 54 inch)
  ROV (Dia > 12 inch)
  Pushed camera (Dia < 12 inch)
ISO 14692-4:Petroleum and natural gas industries — Glass-reinforced plastics (GRP) piping — Part 4: Fabrication, installation and operation.
ASTM D2563: Standard Practice for Classifying Visual Defects in Glass-Reinforced Plastic Laminate Parts.
UUV: Unmanned Underwater Vehicle
Pushed Camera with video for small diameter FRP (less 12 inch)
ROV: Remote Operating Vehicle (> 12 inch)

## Slide 6: Failure modes - Cracks
large damage in the body of the flange.

## Slide 7: Failure modes - Cracks
Internal crack at FRP neck inspected using ROV
Internal crack in FRP pipe inspected using ROV
External crack in FRP pipe

## Slide 8: Failure modes - Cracks & pinhole
Internal crack in FRP piping
pinhole in FRP piping

## Slide 9: Failure modes - Blistering
Blistering

## Slide 10: Failure modes – Weeping (deposits on the outer surface of the pipe)
Weeping observed at this line externally probably due to manufacture defects

## Slide 11: Failure modes – UV attack
Top coat has been removed and fiber exposed due to oxidation related to exposure to UV from sunlight

## Slide 12: Failure modes – Fiber exposed
Structural fibers exposed
Exposed pipe fibers

## Slide 13: Failure modes – discoloration
Complete discoloration and removal of topcoat from FRP pipe
Discoloration of pipe due to leakage

## Slide 14: Visual inspection - salt deposit, discoloration and chemical attack
Salt deposit, discoloration and chemical attack due to leakage of gasket

## Slide 15: Visual inspection– soil settlement
Gap between pipe shoe and base plate
Sign of settlement i.e. foundation of the support has disappeared
Gap between FRP dummy leg and base plate

## Slide 16: Visual inspection– soil settlement
Gap between pipe support and concrete foundation
Gap between the support and foundation (support hanging)

## Slide 17: Failure modes – Corrosion & rust
Corroded nuts and bolts
Rusted nuts and bolts
Corroded nuts and bolts

## Slide 18: Visual defects – FRP piping touching steel or concrete
Steel clamp without neoprene sheet
Pipe directly resting on the steel structure without adequate neoprene pad

## Slide 19: Visual defects – FRP piping touching steel or concrete
Pipe directly resting on concrete without neoprene pad
FRP pipe resting directly on the walls of cooling tower

## Slide 20: Visual defects – piping movement
Dislocation of pipe
Support completely disengaged from the structure for the pipe.

## Slide 21: Visual defects – scratches & Chipping
Scratched pipe surface
Material chipping from main pipe body

## Slide 22: Visual inspection – concrete foundation
Cracks in foundation
Cracks in foundation

## Slide 23: Visual inspection- bellow condition
Cracks in expansion bellow
Pit created in the body of bellow visible in the picture

## Slide 24: Visual inspection- small pipe diameter without stiffeners
Small pipe diameter without stiffeners plates
No reinforcement pad installed for the drain piping
Gauges with four stiffener supports

## Slide 25: Visual inspection- leakage
Seawater leakage and heavily corroded bolts and nuts (washers are missing)
Leakage is visible from the connection with the pump

## Slide 26: Visual inspection- corrosion of steel supports
Corrosion of steel supports
Shoe support for FRP piping bottom up view (completely corroded)

## Slide 27: Visual inspection- High vibration
High vibration in the FRP pipe may be due to missing support

## Slide 28: Visual inspection- road crossing
Road crossing for SW UG pipe without any sign of protection/sign boards showing load carrying capacity.
An 8-wheel vehicle parked next to the header for maintenance work

## Slide 29
Thank You