## Slide 1
INSPECTION & REFURBISHMENT OF
SOIL-TO-AIR CONCRETE CYLINDER PIPE (CCP)
Author : MOHAMMED IMTIYAZ ALI Inspection Engineer SABIC Agri-Nutrients

## Slide 2: CONTENTS
BACKGROUND
PROBLEM STATEMENT
INSPECTION & FINDING
REFURBISHMENT APPROACH AND STAGES
ACHIEVEMENTS

## Slide 3: Background of Seawater and Cooling water CCP Lines
Constructed (30+ years ago) Plant Underground Seawater and Cooling water Network is of CONCRETE CYLINDRICAL PIPE (CCP), connected to above ground Equipment's for Supply & Return system through Elbows & TEE components at Soil to Air Interface (below ground to above ground). These are Pipe STUB’s

## Slide 4: PROBLEM STATEMENT
Plants aging and the STUBs were in service from the commissioning of the plant in supplying the Sea Water and Cooling Water to plant Equipment's, over a period of time some of the STUBs transition zone (Soil to Air) were under severe external weathering effects, as a result developed deteriorations in external cement lining and caused the lining to crack and spall exposing the CS cylindrical, rusting and posing the risk of PIPE RUPTURE.

## Slide 5: Inspection & Findings in Cement Lining of Stubs
STUB’s External Inspection Strategy
  Exposed by excavation 800mm Pipe stub at Soil-to-Air Interface.
  Conduct Hammer tap survey for surface Cement lining and mark cracks & delamination.
  Chip-out to expose the Pipe CS cylinder of Delaminated Cement lining.
Typical Inspection observations as below.
  Exposed CS cylinder external surface observed Rusted. Corrosion extended below ground for a depth of 100-500 mm and Carbon steel cylinder thickness loss.
  STUBs Carbon steel cylinder were found with holes large enough to Pipe Rupture.
  Further Internal Cement lining were found with cracks & pitting.

## Slide 6: Refurbishment stages & Methodology.
Step-1
Grit blast cleaned the exposed external Corban steel cylinder and perform CS Thickness measurement
Step-2
Step-3
Step-4
Step-5
Step-6
If CS thickness loss >10% : Apply Ceramitech CR/HG putty or equivalent to re-profile CS cylinder external surface
If CS thickness total loss and created pinholes: Weld patch plate 4 mm thick extended up to health CS surface.
Weld Crimped wire mesh (50X100X2.6mm) over the re-profiled Carbon steel cylinder.
Apply 20-25 mm thick Cement mortar lining over external CS cylinder with welded mesh.
Apply 6mm thick FRP lamination after curing of Cement lining

## Slide 7: Achievements:
Comprehensive Inspection provided an overview of the CCP Pipe STUB condition.
Extensive repair of the Pipe STUB has extended the integrity.
Shared with SABIC-ATC as a part of Knowledge sharing at Civil-CP Domain meeting.
SABIC-ATC with concerned Affiliate Civil Engineers conducted workshop and developed a unified procedure for Inspection and Repair of CCP STUB’s and Pipeline Pits in OFFLINE and ONLINE condition.
Developed Inspection & repair procedure for STUBs is implemented in every TA to strengthening the plant Seawater Pipe Stubs integrity.
Developed & implement Inspection PM plan for STUB’s External and Internal Inspection every TA.

## Slide 8: Achievements
BEFORE
AFTER
STUB
from Risk of Rupture to Reliable condition
after Inspection & Refurbishment

## Slide 9
Thank You

## Slide 10: External Cracks Soil-to-Air

## Slide 11: CS Cylinder with Corrosion
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 12: Hole in Carbon Steel Cylinder
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 13: Internal Inspection
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 14: Thickness Measurement
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 15: CS surface Re-profiling
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 16: Patch Plate Weld
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 17: Crimped Wire Mesh
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 18: Cement Lining and Curing
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 19: FRP Wrapping and Area Restoration
Inspection & Refurbishment of Soil to Air CCP Stubs – SAFCO - IMA
Classification: General Business Use

## Slide 20
Thank You