## Slide 1
Application of a New Boiler Corrosion & Scale Control Automation
Mohammad Al-Shaikh
Industry Technical Consultant @ Nalco Water

## Slide 2: Primary Water Related Challenges when Operating a Boiler
Mineral Scale/Deposition
  Forms as a result of dissolved minerals in the feedwater exceeding solubility
  Scalants are magnesium, calcium, iron, silica based salts
  Forms insulating material
  Impedes heat transfer
  Can result in equipment damage / boiler shutdown / loss of production
Corrosion
  It causes metal loss in one area of a boiler system, which reduces asset life
  Causes iron deposits (another type of scale) on boiler tubes (energy losses)
  Shutdown, production loss and safety issues

## Slide 3: Steam system: A Holistic approach
We look beyond a single unit operation

## Slide 4: Steam System Treatment
Pre-treatment (oxygen scavengers)
Internal Treatment (scale & corrosion control)
Condensate Treatment (corrosion control)
Proper boiler water treatment prevents deposits and corrosion ensuring reliable and safe production of steam at reduced energy and water consumption and greenhouse gas levels.

## Slide 5: Overall, The Basic Approach To Controlling Boiler Feedwater Chemistry Hasn’t Changed Much In 50 Years
“Test & adjust” approach
  Gather sample
  Test
  Adjust chemical feed
  “Repeat as necessary” ∞
Equipment damage / efficiency loss / production loss
(wasted chemical)
USL
LSL
1
2
3

## Slide 6: Current monitoring practice
Grab sampling and/or on-line methods
  Grab sampling only provides snapshots
Use of indirect methods for determining corrosivity
  pH
  Conductivity
  Dissolved oxygen
  Iron
  Reductant residuals
Notes: Traditional measurements such as pH, product residuals and dissolved oxygen measurements, are indirect methods used for estimating the corrosivity of the boiler feedwater. The industry pays special attention to dissolved oxygen measurement as the key indicator for corrosive conditions.
Please note that historically we referred to reductants as “oxygen scavengers”. With the new technology described on the next slides we now know that reductants do more then scavenge oxygen alone! Therefore we refer to the terminology “reductant”.
Moreover, corrosion products are released every time there is a thermal, chemical, or hydraulic shock to the system, and current iron monitoring practices often lead to questions on the validity and interpretation of the data produced. Grab sampling only provides a snapshot, but if the full extent of the events could be made visible, responses could be developed to minimise corrosion and iron transport to critical heat transfer surfaces.
The traditional measurements are still important as they relate to boiler manufacturers specifications or industry standards.

## Slide 7: …And Is Still Largely Centered Around Testing The Water After It Is In The Boiler
An event taking place here….
…could take hours or days to show up here!
By then, its far too late to detect or remedy

## Slide 8: Causes of Boiler System Failures
Note that BFW Quality is considered to be the cause of most boiler system failures
Chart: 
| Poor BFW Quality | Condensate Corrosion | Chemical Control | Other
 | 0.67 | 0.18 | 0.07 | 0.08
Poor BFW Quality
Chemical Control
Condensate
Corrosion
Other

## Slide 9: Pre-boiler Corrosion
Chemical Factors
Pre-boiler corrosion
Temperature
Fluid Velocity
Outages
Metallurgy
Retention Time
DA Performance
FW Demand
pH
O2
Scavenger Residual
Other Contaminants
Mechanical & Operational Factors
Measuring the Oxidation Reduction Potential (ORP) in the bulk water is measuring the corrosivity of the system
@T ORP is the key performance measurement
Notes: In understanding preboiler corrosion it is important to realize that this can be a complicated ‘space’ (topic) with many variables. Also many of these topics are not simply confined to preboiler corrosion but really apply to all corrosion phenomena in the boiler water, and other water industries.

## Slide 10: EPRI Cycle Chemistry Guidelines for Fossil Plants: Phosphate Continuum and Caustic Treatment, Jan 2004, Appendix B.
“Thus ORP should be used to control the oxidizing power of the feedwater in all-ferrous systems or, and more importantly, the reducing power of the feedwater in mixed-metallurgy feedwater systems.”
“The future direction should be to develop the technology to measure ORP in-situ in feedwater, and to extend the mixed-potential model for use at the elevated temperatures, where components are actually in contact with high temperature water, such as in the boiler.”

## Slide 11: BFW Oxidation / Reduction Potential (ORP) Monitoring
ORP correlates to the corrosion stress of the aqueous environment
    More oxidizing - can be more corrosive
    Potential difference between measuring and reference electrodes
    More reducing – can be more passive
ORP is influenced by temperature, pH, O2, dissolved solids, etc.
ORP = Oxidation / Reduction Potential.
+
0
-

## Slide 12: @T ORP vs RT ORP (at Temp vs Room Temp –from economizer outlet)
ORP Cell Internal Configuration
Notes: So why not use regular ORP measurements on a cooled feedwater sample (“Room Temperature ORP”)
KEY TAKEAWAY: @T ORP (black line) is fast and very sensitive to system changes even when compared to RT ORP. Notice with the room temperature ORP (red line) barely detected the redox event. Highlight the small bump with your laser point.
RT ORP means the sample stream is cooled, then measured using the same type of ORP instrument that is commonly used for biocide control in CW systems.
This slide discusses a trial in a 200MW coal-fired power plant and shows how @T ORP responds to oxygen ingress upon startup after a trip.
During that time we not only optimized the Elimin-Ox feed to maintain the optimum ORP setpoint as the graph shows, and successfully manage the stress of the startup, but the plant has also set records for speed of unit start-up after a trip. It now takes only 5 hours to come up to full load with no holds on silica or TDS. It normally took 2-3 days (48-72 hours). This translates to approximately $134,000 savings per trip based on the cost differential between this customer’s generating costs and the cost of replacement power.

## Slide 13: LOOKING INSIDE Without Opening Your Boiler
High
Reductant feed
Low
High
Feed water corrosiveness
High
Low
Regular
control
NCSM control
ORP@T patented sensor allows us to DIRECTLY MEASURE Feed Water CORROSIVENESS
Feed Water Corrosion Stress Monitor (mV)
+300
+200
+100
0
-100
-200
-300
-400
-500
-600
Pitting
Close to Pitting Zone
High General Corrosion Rate
Low General Corrosion Zone
Notes: NCSM = Nalco Corrosion Stress Monitor

## Slide 14: Scale and deposit control
Ions and particles in the boiler feedwater concentrate in boiler and can form scale and deposits resulting in lower efficiency and possible tube failure
Treatment program contains unique inert, fluorescent tracer
Can be used to measure and control the level of Antiscalant in the system
Sample Water
Flow
Cell
Emission
Filter
TRASAR
Detector
Light
Source
Excitation
Filter
Notes: By preventing deposition of corrosion products and hardness scale, clean heat transfer surfaces are assured, resulting in operational efficiency and reduced risk on waterside corrosion. Heat losses via the blowdown are minimised by improved blowdown practices.
Nalco programmes can contain an inert trasar that can be used for controlling the feed of the internal treatment program and for determining the cycles of concentration.

## Slide 15: Real time Internal Treatment Control
Realtime hardness excursion over the weekend.... and takes swift action to handle the system stress.

## Slide 16
Condensate
Feed water
Boiler
Deaerator
Process
DCS
Blowdown
Oxygen Scavenger
Internal treatment
BFW
Analyzer/Controller
Boiler Water
Analyzer/Controller
System Assurance Center
Integrated solution
Integrated solutions
bring more value.
The most effective means of Energy and Water Optimization is Automated Cycle Control

## Slide 17
Chemistry
internal treatment chemistry
Monitor
TRASAR with Fluorometer in feedwater
Control
Chemistry dosage in feedwater
Chemistry
Oxygen scavenger chemistry
Monitor
Corrosion stress with ORP@T in feedwater
Control
Chemistry dosage in deaerator
Communication
Wireless gateway
Website
dashboard and historical data
Remote experts
System Assurance Center
24/7/365
Scale treatment
Corrosion treatment
Digital
PI
PI
Sample conditioning
pH, conductivity
Fluorometer

## Slide 18: Overcoming Steam Generation challenges
Energy cost, carbon footprint
Repair cost, production stop, operator safety
Water usage
Scaling, low cycles
Continuous advanced monitoring and control of internal treatment and oxygen scavenger chemistry prevents scaling and corrosion, maximizes heat transfer, allows higher cycles, protects assets and operators, prevents stops.
Remote expert monitoring and alarming by System Assurance Center & Web based platform
Low cycles
Tube ruptures due to scale and corrosion
Challenge
Root Cause
Real Time/Automation

## Slide 19
MINIMIZE Water
Make-up water intake
MAXIMIZE Results
Energy usage, carbon footprint
Steam production
Reliability and safety
OPTIMIZE Costs
Operation
Energy, water
Assets, repairs
14.2M
GJ
ENERGY
785k
tonnes CO2
AIR
11.4M
m3
WATER
Saved in 2020

## Slide 20
Thank You