## Slide 1
Closed Cooling on TRACK Innovation
Increasing reliability and reducing environmental impact
Presented By:
Mohammad Al-Shaikh
Industry Technical Consultant,
IMEA Region
JUBCOR
CONFERENCE & EXHIBITION
2024
INNOVATIVE SOLUTIONS FOR CORROSION CHALLENGES

## Slide 2
Royal Commission review of environmental regulations: global trends for stricter limits
Create Maintain Value: innovation part of our process Saudi vision 2030 requires water management excellence and minimal footprint
ENGAGE
ENGAGE
DO
Value
Communication
Metrics
(Measure/Audits)
Continuous
Improvement
Innovation
Key
Business Drivers
System
Assurance

## Slide 3
Closed Cooling System controlling the process temperatures
High efficiency heat exchange for operational reliability
High water quality make-up eliminates scale under high stress conditions
Current practice: Molybdate Or Nitrite with borate buffer for corrosion control at high pH
Treatment control is essential to maintain corrosion inhibition performance
  Nitrite is oxidized to nitrate e.g. by bleach in make-up water
  Nitrite is readily reduced to N2 gas by bacteria when biodegradable organics enter the loop
  Process leaks promote biofilm growth and nitrite reduction, control can be challenging
SDS of Nitrite has several hazard symbols; direct disposal of treated loop no option
Molybdate in the wastewater is regulated by RC. Discharge level is very low < 0.01 mg/L
Nalco Water R&D developing the next generation of treatment
  Responsible Care: Looking for more sustainable solution
  Laboratory testing successful: static and dynamic pilot tests show excellent corrosion protection
  Industry technical trials show excellent performance during hydrocarbon leak into cooling system
New biostatic technology minimizes water footprint by lowering blowdown needs
Closed Cooling: controlling your process
Shell and Tube
Heat Exchanger

## Slide 4
Cooling Treatment Challenges
Scale
formation occurs when impurities form hard, dense crystals.
Corrosion
is the oxidation of metals, supported by water.
Fouling
is the accumulation of dispersed solids in water.
Microscopic organisms
in water can cause system and health problems.
Process leaks pose biofouling challenges & high operational costs
High purity water as make-up, discharge not allowed due to treatment chemistry
Cooling system leaks drain the closed loop, treatment residual control critical

## Slide 5
Holistic treatment program development
Advanced corrosion and biofouling control
  Cost effective and safe treatment
  Chlorine & non-oxidizing biocide compatible
  Mild Steel and yellow metal corrosion inhibition
  Easy monitoring and control
Additional Program improvements
  Biostatic treatment
  Very high buffer capacity
  Direct water disposal depending on local regulation
Aim to safeguard production:
  Debottleneck closed cooling

## Slide 6
TRAC400: Closed Cooling Treatment innovation
6
Sustainable Technology
  Non-P
  Non-NO2
  Non-Boron
  Non-Molybdate
  High buffer capacity
  Compatible with Nitrite and Molybdate
  Chloride and sulfate tolerant
  Biostatic, (bio)chemically stable actives
Robust Closed Cooling Treatment

## Slide 7
Nalco Water Global R&D developed and tested
  Robust program performance shown
  Extensive bench flow loop (stress) testing
  Best performer identified, patent protection pending
  Pilot plant production successful for industrial trial
Regional trials at KAUST
  Marafiq service water used for closed loops
  Hydrocarbon contaminated water from local closed loops
  Ammonia and Microbio contaminated real water samples
Industrial application proven concept
  High Temperature, challenging cooling system
  150 m3 loop VDU (hydrocarbon leaks during stress)
  Excellent corrosion control and very low iron values
TRAC400 Development process

## Slide 8
Comparative performance superior performance with non-toxic, innovative chemistry
Delivering Performance
KPIs
Filming/buffering Amines
Nitrite/ Borate
Molybdate/ Borate
Robust corrosion Protection
Toxicity profile
Buffering capacity
Biostability
Nitrite overlay compatibility
N/A
Incumbent Treatments
Competitor Offering
TRAC400
Triple-P Inhibition
non-Toxic inhibitor
No-Borate or amines
High buffer capacity
Biostatic treatment
Robust performance tolerant to operational variability
Cost

## Slide 9
Large or critical loops: 3D TRASAR online control
  Corrosion, conductivity, pH, TRASAR in real time
  Web based 24/7 system assurance
  Spot checks on water quality, actives and microbio
Other loops: TRASAR Pen Fluorometer
  Spot checks on treatment dosed, pH, Conductivity
  Spot checks on water quality, actives and microbio
  All uploaded for digital reference and trending
Change management to TRAC400
  Target dose rate selected based on chloride levels
  TRASAR measures inhibitor dosed, actives target linked
  Lower conductivity band (less mS/cm per ppm), similar pH
  TOC contribution 150-200 ppm, biostatic & HC leak tolerant
Monitoring and control
Data digitally-enabled in the cloud with SAC analyses and reports performance, manage alarms and provide recommendations 24/7 to deliver performance.
State of the art controller (Intuitive color touch-screen, multiple language platform)
Smart sensors to determine corrosion, scaling tendency, and critical water and treatment parameters
Enhanced monitoring and control options

## Slide 10
10
10
System Details
Refinery high temperature closed cooling system
Demi Water make-up due to >100C operating temperatures
Treated with ~3000 ppm TRAC109
pH=11,2, no CO2 ingress due to nitrogen blanketing.
Periodic water leaks out of the system periodic top-up
System conductivity 2000-5000 µS/cm (average 3175 µS/cm)
Mild Steel Corrosion under good control 0,03 mpy (<1 mpy target)
INNOVATION
TRAC400, new nitrogen, borate and molybdate free product for sustainable closed loop treatment:
Corrosion Coupons spotless, at 0,02 mpy well below target
Rapid protection, stable actives level one week after first fill
System conductivity 2000 µS/cm (slowly dropping to 1700 µS/cm
Actives follow slow conductivity drift, pH stable at 11,2
Meeting customer targets in discharge water quality
No biological growth recorded, despite hydrocarbon leak detected
CASE STUDY
Refinery makes step change in closed cooling treatment sustainability
ANNUAL SAVINGS
1 and 3 month coupons
both confirm mild steel
corrosion control to
0,02 mpy
Well below 1 mpy limit
No Iron dissolution: constantly below detection limit of
0,02 ppm
SOLUTIONS
TRAC400, Novel non-toxic closed loop treatment program
3D TRASAR® Technology for Cooling
Eliminated 2 hazard symbols from the SDS
Eliminating
Nitrite and Borate
From treatment
Under high temperature conditions

## Slide 11
SOLUTION
11
11
APPLICATION
Steel mill struggling with corrosion in the closed loops of the blast furnace
System Volume: 90 m3
Make-up: Lime softened + Basic Ion-exchanged, inherently corrosive water [50 ppm Cl, 110 ppm SO4]
ISSUES
Significant localized & general corrosion (2-18 mpy) exceeding site KPI of <0.8 mpy
Total iron levels as high as 16 ppm despite sockets & magnetic filters in place (Site KPI < 5ppm)
Molybdate based treatment currently in place
INNOVATION
TRAC400, a new borate, nitrite and molybdate free product for sustainable closed loop treatment:
Excellent mild steel corrosion coupon results: <0.2 mpy, well below target
No localized corrosion at optimized dosing
Total iron of 4-6 ppm achieved with low blow down rates
SUCCESS STORY
Steel Mill reduces corrosion by 95% using Nalco Water’s new, high-performing, green closed loop chemistry TRAC400
RESULTS
Excellent Mild Steel and Yellow Metal corrosion control
<0,2 mpy
Well below site KPI (<0.8 mpy)
Total Iron levels 4-6 ppm achieved with
low blow down rates
TRAC400, Novel non-toxic, borate, nitrite and molybdate-free closed loop treatment program 3D TRASAR® Technology for Cooling
Period | Corrosion Rate (mpy) | N# Days | Description
Historical Data | 1.5 | 71 | Localized (3 mils)
 | 1.7 | 55 | Localized (7 mils)
 | 18.3 | 45 | General
 | 4.0 | 98 | Localized (17 mils)
Product Introduction | 0.3 | *30 average | Localized (2-4 mils)
Coupon 1 | 0.2 | *29 average | General
Coupon 2 | 0.2 | 20 | General
Coupon 3 | 0.1 | 77 | None
4.0 mpy (98 days)
18.3 mpy (45 days)
Historical Results
0.2 mpy (20 days)
0.1 mpy (77 days)
TRAC400 Application

## Slide 12
Reach out.
THANK YOU
malshikh@ecolab.com
+966 5005 88 232
Calle Cualquiera 123, Cualquier Lugar
JUBCOR
CONFERENCE & EXHIBITION
2024
INNOVATIVE SOLUTIONS FOR CORROSION CHALLENGES